3D Modeling and Simulation of Fast Fuses for Power Semiconductor

Devices Protection

Adrian Plesca

“Gh. Asachi” Technical University of Iasi

Blvd. Dimitrie Mangeron, 51-53, Iasi - 700050, Romania

aplesca@ee.tuiasi.ro

Abstract— It is important to know the thermal behaviour of a fast fuse for an optimized design as well as for a right choice of the fuse rating due to protect the power semiconductor. A 3D thermal model was developed in order to study the temperature distribution for a fast fuse. In this model the thermal behaviour of the fast fuse depends on the design of the fuselink elements, the material parameters and the ambient conditions. The simulated temperatures were compared with measured temperatures at defined points on the fuse.

Keywords— 3D thermal model, fast fuse, temperature distribution

# Fuses for power semiconductors

The underlying principle associated with fuses is that a relatively short piece of conducting material, with cross-sectional area insufficient to carry currents quite as high as those which may be permitted to flow in the protected circuit, is sacrificed, when necessary, to prevent healthy parts of the circuit being damaged and to limit the damage to faulty sections or items to the lowest possible level.

Fuses incorporate one or more current-carrying elements, depending on their current ratings, and melting of these, followed by arcing, occurs when excessive overcurrents flow through them.

From power semiconductor overcurrent protection point of view a special fuses were made, so called fast fuses. These kind of fuses have a special construction of the fuselinks because of their specific geometry.

# 3D thermal model of a fast fuse

Taking into account the thermal phenomena complexity for a fuse it is very difficult to study the heating processes both in steady-state or transitory operating conditions, using the traditional analytical equations. Approaches to simulate these processes have already been made in earlier work. In [1] the temperature distribution, and the thermal and electrical resistances of basic elements of the fuses are described by exact or semi-empirical analytical equations, and combined with iterative solution procedures. In [2] the fuselink is represented by an equivalent R-C network. Other simulations discretize the fuselink including its conductor according to Finite Element, [3]. Because of the typical geometry of fuses a three-dimensional discretization is generally necessary, at least for the heat diffusion problem. In [4] a commercial FEM package has been used to model heating of relatively simple fuse geometries without notches and with one single notch, respectively. In [5] a Windows based program code for modeling complete fuses, including M-Effect, using the Finite Volume Method, has been developed.

While former work, due to limited computer capabilities, often had to concentrate on partial problems or on parts of the fuse geometry only, the progress in computer technology enables the modelling of more and more complex structures in less time. It has therefore been the aim of this work to develop a 3D model of a complete fast fuse used for power semiconductor protection.

The starting point is the power balance equation for each volume element dV, in the integral formulation, [6]:

(1)

where:

T means the temperature of element [ºC];

j – current density [A/m2];

σ – electrical conductivity [1/Ωm];

ρ – material density [kg/m3];

c – specific heat [J/kgºC];

λ – thermal conductivity [W/mºC].

The left term of before equation (it exists only in the fuse conductor elements), denotes the heating power from the current flow. It is in balance with the heat stored by temporal change of temperature, and the power removed from the element by thermal conduction.

Taking one's stand on the above thermal equation, first of all a 3D model for a fast fuse has been developed using a specific software, the Pro-ENGINEER, an integrated thermal design tool for all type of accurate thermal analysis on devices. The subject was a fast fuse type aR with rated current by 400A, rated voltage about 700V and rated power losses of 65W. The 3D model had taken into consideration all the component parts of a fast fuse: outer cap, end tag, rivet, inner cap, ceramic body, fuselink and granular quartz. It was considered a simplified geometry for the rivets.

The granular quartz which is filling up inside the ceramic body of the fuse have been modelled by a solid and also many small solid parts which fill all the gaps from the fuselinks.

# 3D thermal simulation of the fuse

It was considered a real application when this type of fast fuse is used to protect against overcurrents a three-phase power semiconductor rectifier. The current which flows through the converter branches and therefore through the fast fuses is about 315A. Taking into account that the rated power losses for the fuse is about 65W and the rated current is 400A, the rated resistance will be,

(2)

Hence, at a current with the value of 315A results a power losses by,

(3)

In this case, because the fuse has three fuselink elements and assuming an equal distribution of the current flow, every fuselink will dissipate 13.23W.

For all thermal simulations a 3D finite elements Pro-MECHANICA software was used. From experimental tests [2], it was computed the convection coefficient value for this type of fast fuse, kt = 42.47 [W/m2ºC]. Hence, it was considered the convection condition like boundary condition.

Further on, some steady state thermal simulations have been done. The temperature distribution inside the fuse is shown in the figure 1. The maximum temperature, on the fuselinks is 229.4ºC and the minimum, on the surface of the ceramic body, is about 80ºC.

Fig. 1.   Temperature distribution through left side fuselink at

24.45% cross section

As it can see from the pictures, the maximum temperature is obtained on the fuselink elements in the centre. This is explained because of the notches made on the fuselinks in order to clear the fault current as soon as possible and to interrupt the electric circuit without high overvoltages. It was considered that every fuselink element has to dissipates the same quantity of heat, hence the maximum temperature is the same for every one. Of course, there is a thermal influence among these fuselink elements because of their geometrical site.

To validate the 3D thermal model some experimental tests have been done in the same conditions like thermal simulation case. Using proper thermocouples, it has measured the temperature on the fuse ceramic body on the proximity sides of the fuselinks. The measurement points were placed on the lateral sides and upper side of the fuse body.

From the experimental data it can observe a maximum temperature in the middle of the fuselinks and the minimum temperatures on the end-terminals of the fuse, because of the outer caps which act like heatsinks for the fuselink elements.

Higher temperature values are for the upper surface of the fuse as compared to lateral side because of the thermal influence of the lateral fuselinks. Of course, there are different temperature values resulted from experimental tests with respect to simulations because of measurement errors, thermal model simplifications, unbalanced current distribution through fuselinks and mounting test conditions. The thermal model has not included the different types of busbar connections. Anyway, the maximum difference between experimental and simulation results is less than 3ºC.

# Conclusions

Further on, the main conclusions of the simulation study as regards temperature distribution at fuses for power semiconductors protection are presented:

- because of very complex thermal phenomenon the analysis of fast fuses thermal field can be done using a specific 3D FEM software; in this way it can be calculated the temperatures anywhere inside or on the fuse;

- it can observe a maximum temperature in the middle of fuselinks and the minimum values at the ends; also, there is a thermal influence among fuselinks that leads to different temperature values on the fuse surfaces;

- there is a good correlation between experimental and simulation temperature values;

- using the 3D simulation software it can improve the fast fuse designing that implies a better protection for power semiconductors and also to get new solutions.

# Acknowledgement

The author has a pleasure to acknowledge that described investigations have been carried out in the frame of Marie Curie European Reintegration Grant MERG-7-CT-2005-014990 within the 6th European Community Framework Programme.

# References

R. Wilkins, “Steady-state current sharing in fuses with asymmetrical arrangements”, Forth International Conference on Electric Fuses and their Applications, ICEFA, Nottingham, UK, 1991, pp.28-33.

A. Pleşca, “Overcurrent protection systems for power  semiconductor installations”, PhD Thesis, Iaşi, Romania, 2001.

L. Fernández, C. Cañas, J. Llobell, J. Curiel, J. Aspas, F. Ruz, and F. Cavallé, “A model for pre-arcing behaviour simulation of H.V. full-range fuse-links using the finite element method”, Fifth International Conference on Electric Fuses and their Applications, ICEFA, Ilmenau, Germany, 1995, pp.162-168.

D.A. Beaujean, P.G. Newbery, and M.G. Jayne,  “Modelling fuse elements using a C.A.D. software package”, Fifth International Conference on Electric Fuses and their Applications, ICEFA, Ilmenau, Germany, 1995, pp.133-142.

M. Lindmayer, “3D simulation of fusing characteristics including the M-Effect”, Sixth International Conference on Electric Fuses and their Applications, ICEFA, Torino, Italy, 1999, pp.13-20.

A. Wright, and P.G. Newbery, Electric Fuses, 2nd edition, The Institution of Electrical Engineers, London, United Kingdom, 1995.